## Data Sheet (311-3)
IEA Implementing Agreement for Hydropower Technologies and Programmes
Annex-2: Small-Scale Hydropower; Subtask B2 "Innovative Technologies for Small-Scale Hydro"
IEA Annex-2 STB2 Data Sheet about Innovative Technology（311-3）
| 1 | Project Title | Subject | Micro Kaplan Turbine | Attachments and Additional Remarks
|  |  | Commercial Name | Hydro Agri
| 2 | Project Classification | Technological Categories | 3. Construction (Civil Work, E&M)
|  |  | Target Categories | 31. Cost/Time Reduction
|  |  | Key Categories | 311. Utilization of Previous Facilities
|  |  | Key Words | Low-head water turbine, Integrated power generation system, Use of existing equipment, Agricultural water channel, Automatic flow control
| 3 | Organizations | Funding | Electric Power Development Co. Ltd
Nakagawa Suiryoku Co. Ltd
|  |  | Development Organization | Electric Power Development Co. Ltd Nakagawa Suiryoku Co. Ltd.
Nakagawa Suiryoku Co. Ltd
| 4 | Abstract | A unitary 30kW power generation system comprising a water turbine, generator and control system packaged in a single unit for installation in existing agricultural water channels with low head, and designed to minimize associated construction costs.
| 5 | Features and Advantages | Technological Performance | - A small Kaplan water turbine for use with low head, and permitting automatic flow control.
- Designed solely for installation in channels without bypasses, thus permitting operation without restriction of flow.
- Multiple units may be installed in the same channel as a cascade and using the same head.
- The water turbine-generator may be removed or installed without interruption of flow.
|  |  | Cost Performance | - Since only the generator unit assembled in factory is installed in the agricultural water channel, associated construction costs may be reduced.
|  |  | Environmental Performance | - Efficient use of unused head without major construction costs.
| 6 | Scope of Application | Basic Specifications | Turbine : Vertical shaft Kaplan Turbine, Generator : Vertical shaft 3 Phase Induction Generator Head: 2.0m, Flow: 2.4m3/sec, Output: 30kW, Speed : 204min-1
|  |  | Purpose of Application | Agricultural water channels
|  |  | Technological Conditions for Application | Channel ; Wide : 2.1 - 2.9m, Height : 1.2 - 4.0m Head: 2.0 - 3.0m, Flow: 0.8 - 2.4m3/s
| 7 | Status of Project | Present Status | Commercial Stage
|  |  | Period | Year of Commencement : Mar. 2004 Year of Completion : Sep. 2005
| 8 | Results of Application | Results of Experiments or Demonstration Tests | Fall in upper main channel No.7, Hyakumura, Nasushiobara City, Tochigi Prefecture Output: 30kW, Max. Flow: 2.4m3/sec (Non-Irrigation period : 1.29m3/s), Effective head: 2.0m Operation: High-voltage system (with reverse power flow) Completion: April 2004 Site tests for practical application were performed under connecting to power grid line. Hydro Agri – 1 unit
|  |  | Results of Sales/Practical Applications | Fall in upper main channel No.2, 5, 6 and 7, Hyakumura, Nasushiobara City, Tochigi Prefecture Head: 2.0m, Flow: 2.4m3/sec Hydro Agri – 4 units
| 9 | Evaluation | Contribution to Cost Reduction | Units are installed for drop work in a water channel. This can lead to process reduction as well as a reduction in civil engineering work.
|  |  | Enlargement of Applicability | The application has been extended to agricultural waterways that were not used for conventional hydraulic power generation.
| 10 | References | Hydropower System provided on low fall in Agricultural Open Channel (in Japanese)
| 11 | Appendices | Fig. 1 Power Generation System for Open Channels – Power generation Equipment Fig. 2 Power Generation System for Open Channels – Plan and Section Views of Demonstration and Test Unit Fig. 3 Unit installed in Irrigation Channel
| 12 | Inquires | Organization / Department | Electric Power Development Co. Ltd., Hydropower Engineering Division
|  |  | Ａｄｄｒｅｓｓ | 6-15-1 Ginza, Chuo-ku, Tokyo
|  |  | TEL・FAX | Tel： 03-3546-2211 Fax： 03-3546-9423
|  |  | URL・Email | www.jpower.co.jp
Fig. 3 Unit installed in Irrigation Channel
Fig. 1 Hydro Power Generating System
installed in Open Channel
Fig. 2 General Arrangement of Pilot Unit
installed in Open Channel